POOL / SPA  SUBMITTAL REQUIREMENTS

As required by Bureau Veritas North America, Inc.

ALL INFORMATION MUST BE FILLED IN, CHECKED OR MARKED N/A

______Application

______Local Municipal Approval

______Site Plan of pool/spa location showing any overhead lines

______1 copy of manufacturer specifications and plans (must be at site)

The following items, views and details shall appear on all plans:

| ______1. | Location of pool must be so that any overhead service entrance cables are 22.5' from the water level in any direction. If installing a diving board or platform a distance of 14.5' must be maintained. |
| --- | --- |
| ______2. | If in-ground pool, consideration for any underground utilities should be taken. No non-pool related underground wire within 5' of pool wall unless in approved conduit. |
| ______3. | Pool wiring: ______a. Feed wires and branch circuit wires need to be installed in conduit. NM (romex) allowed indoors only in residential. ______b. Conduit must be of the following type: RMC, IMC, LFNMC, RNC |
| ______4. | Bonding: |
|  | ______a. All metal parts of structure & equipment must be bonded ______b. Exception: isolated parts < 4" in any dimension and do not penetrate the pool structure < 1" ______c. Bonding with a 8 AWG or larger conductor |
| ______5. | Grounding: |
|  | ______a. Grounding conductors must be insulated |
|  | ______b. No splices in conductors must land in terminals |
| ______6. | Lighting: |
|  | ______a. Underwater Wet-Niche: ______1. Installed where top of fixture lens is not less than 18" below water line ______2. Bonded and secured to shell requiring a tool for fixture removal ______3. Low voltage lines from UL listed transformer separate from line voltage ______4. Over 15 V must be GFCI protected ______5. Connections in Wet-Niche must be potted ______6. Metal parts in contact with pool water need to be corrosionresistant ______7. Junction boxes for pools must be UL listed for use |
|  | ______b. Dry-Niche: |
|  | ______1. Provided with means for drainage of water |
|  | ______2. One equipment-grounding conductor for each conduit entry |
|  | ______c. No-Niche: |
|  | ______1. UL listed for use |
|  | ______2. Installed in forming shells connected for each conduit bracket |

| ______7. | Receptacles and Equipment Locations: ______a. Receptacles for circulation and sanitation systems of pools shall be permitted to be located between 5' and 10' from pool wall and be a single rec. GFCI protected with ground and be of a locking type. ______b. Permanently installed pools require a receptacle at least 10' but no more than 20' from pool wall ______c. All exterior receptacles within 20' of pool walls need to be GFCI protected ______d. An accessible disconnecting means for all equipment except lighting shall be located within site of equipment and not less than 5' from pool wall |
| --- | --- |
| ______8. | Lighting Outlets: ______a. Existing lights less than 5' from pool wall and at least 5' above the water level need to be GFCI protected ______b. New installation above the pool or within 5' of pool wall need installed at least 12' above the water line ______c. Indoors lights with a totally enclosed fixture or identified for use can be 7'6" above the water if GFCI protected ______d. Switches other than ones UL listed need to be at least 5' from pool wall |
| ______9. | Entrapment protection: ______a. All pool and spa suction outlets shall conform to ANSI/ASME A112.19.8M or be a drain grate of at least 12" X 12" or larger or an approved channel drain SPAS AND HOT TUBS |
| ______10. | Spas and hot tubs follow same rules as pools except for: ______a. Factory assembled units can connect to power source with a 15" cord to a GFIC outlet ______b. Bond all metal parts within 5' of spa or hot tub ______c. GFCI protection to spa or hot tub not required if pumps, heaters, lights and other electrical equipment is protected by self contained GFCI UL listed from factory ______d. No wall switches or appliances within 5' of hot tub or spa ______e. Indoor locations: Light fixtures permitted less than 7' 6" over spa or hot tub if GFCI protected, enclosed with glass or plastic lens, no exposed metal parts and listed for damp locations. REQUIRED BARRIERS |
| ______11. | Barriers are designed to provide protection against potential drowning by |

restricting access to swimming pools, hot tubs and spas:

______a.  The barrier must be at least 48" to the top above the finish grade ______b.  Openings in barrier shall not allow a 4" diameter sphere to pass    through

______c.  Access gates for pedestrians shall have a self locking device and be of a self closing type

______d.  The release mechanism for the gate must be at least 54" from the bottom of the gate or be located at least 3" below the pool side of the top of the gate

______e.  If a wall of a dwelling serves as part of the barrier all doors that directly access the pool need to be equipped with an audible alarm

______f.  Where an above ground pool serves as the barrier the ladder or steps need to be capable of being locked, secured or removed to prevent access    ______g.  Barriers shall be constructed and located away from structures, equipment or similar objects to prevent them from being used to climb on or over the barriers

______h.  Barrier exceptions – hot tubs or spas with a safety cover complying with ASTMF 1346 shall be exempt from these provisions.

| ______12. | Decks: |
| --- | --- |
|  | ______a. Decks built 30" high above grade require guards ______b. Plans for deck need to be submitted for approval at time of permit application ______c. Deck footing must be a minimum of 36" deep ______d. Access to decks around pools must meet above barrier requirements ______e. Decks cannot cantilever on above ground pool walls without proof from the manufacturer that the pool is capable of supporting the deck |
| ______13. | Portable or storable pools: ______a. Cord connected pumps shall have a double insulated cord and ground that grounds all internal non-accessible metal parts ______b. Electrical equipment needs protected by GFCI circuit ______c. Lights for storable pools need to be UL listed with no exposed metal parts |

I have read and understand the above requirements for the installation of swimming pools and/or spas.  By signing this document I agree to install my pool/spa in accordance with the Pennsylvania Uniform Construction Code Law.

____________________________________________   ____________________________________________ Print Name 	 	 	 	 	 	 	Signature

___________________________________________

Date

# THIS COMPLETED FORM MUST BE TURNED IN WITH PLANS

July 18, 2006